## Deviation test 42FIT4000
Flowmeter | Tank ID | Chemical | Injectionpoint | Range 4 mA [kg/t] | Range 20 mA [kg/t] | Density SAS
42FT4000 | 42TB001 | Scale Inhibitor A | Umbilical Riser Gjøa | 0 | 54.2 | 1.229
Accuracy test: | 1
Date | 2024-02-27
Flowtransmitter | 42FIT4000
Chemical name | Scale inhibitor A
Last tested | 2022-12-12
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 50 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
5. Reset the totalizer before each test
BEFORE ADJUSTMENTS
Time [minutes] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x] | Test [1] | Test [2] | Date of Test: | 2024-02-27
1 | 20.9234 | 19.1234 | N/A |  |  |  | Setpoint Pump Stroke Length [%] | 50 | 35 | Flow Transmitter: | 42FIT4000
2 | 20.9342 | 19.1542 | N/A | [6 empty] | Flow Measurement Range: | 0 - 54,20 kg/hr
3 | 21.2341 | 19.1432 | N/A | Zero calibrated Ext flowmeter |  |  | 42FIT4000 - FlowMeas [kg/hr] | 21.1252 | 12.1356 | Last Calibration Date: | 2022-12-12
4 | 20.7542 | 19.1432 | N/A |  |  |  | Ext. Flow - FlowActual [kg/hr] | 19.1469 | 11.1368 | Coriolis Sensor Fabric New | 2009-07-01
5 | 20.5843 | 19.1543 | N/A |  |  |  | Mass Flow Deviation [kg/hr] | 1.9783 | 0.99879
6 | 21.4953 | 19.1495 | N/A |  |  |  | Mass Flow Deviation [%] | 10.3323 | 8.9684 | Total Result from all tests
7 | 20.9428 | 19.1535 | N/A | [6 empty] | Average Mass Flow Deviation [%] | 9.6503
8 | 20.8424 | 19.1459 | N/A |  |  |  | 42FIT4000 - TotalizerMeas [kg] | 3.623 | 2.041 | Average Totalizer Deviation [%] | 10.794
9 | 21.9485 | 19.1525 | N/A |  |  |  | Ext. Flow - TotalizerActual [kg] | 3.2154 | 1.874 | Total Deviation Meas/Actual [%] | 10.2221
10 | 21.5932 | 19.1496 | N/A |  |  |  | Totalizer Deviation [kg] | 0.4076 | 0.167
[7 empty] | Totalizer Deviation [%] | 12.6765 | 8.9114 | FlowMeas / FlowActual [%] | 109.6503
Time [minutes] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃] | [6 empty] | TotalizerMeas / TotalizerActual [%] | 110.794
1 | 1166 | 15 | 16.3 |  |  |  | 42FIT4000 - Temperature [℃] | 15.04 | 15.04 | Combined result of FlowMeas and TotalizerMeas [%] | 110.2221
2 | [6 empty] | Ext. Flow - Temperature [℃] | 16.28 | 16.14 | Total Deviation Ratio Meas/Actual | 1.1022
3 | 1166 | 15.1 | 16.2 |  |  |  | Ext. Flow - Density [kg/m3] | 1166 | 1164.4
4
5 | 1166 | 15 | 16.3
6 | [6 empty] | Settings | Before | Calculated
7 | 1166 | 15 | 16.3 |  |  |  | Flow Calibration Factor [kg/s2] | 1352.2757 | 1226.8639
8
9 | 1166 | 15.1 | 16.3 |  |  |  |  | Before | After
10 | [6 empty] | Fine adjustments for FCF [kg/s2] | 1226.8639 | 1226.8639
Results | 42FITXXXX | Extern flowmeter |  |  |  |  | Other Settings | Before | After
Average Mass flow [kg/hr] | 21.1252 | 19.1469 |  |  |  |  | Damping tau Analog Out [sec] | 0 | 10
Average Temperature [℃] | 15.04 | 16.28 |  |  |  |  | Damping filter for Local Display [sec] | 0 | 10
Average Density [kg/m3] | N/A | 1166 |  |  |  |  | Damping Samles [Samples] | 50 | 65
[7 empty] | Filter Frequency tau [sec] | 0 | 10
[7 empty] | Density Measurement | On | Off
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 3.623 | 3.2154 |  |  |  |  | AFTER ADJUSTMENTS:
Totalizer [L] | 2.9479 | 2.7576 |  |  |  |  | Average values for Deviation Test [x] | Test [3] | Test [4]
[7 empty] | Setpoint Pump Stroke Length [%] | 50 | 35 | Date of Test: | 2024-02-27
Results Flowglass | [9 empty] | Flow Transmitter: | 42FIT4000
Volume delivered from Flowglass [L] | N/A | [5 empty] | 42FIT4000 - Mass Flow [kg/hr] | 19.1341 | 11.1289 | Flow Measurement Range: | 0 - 54,20 kg/hr
[7 empty] | Ext. Flow - Mass Flow [kg/hr] | 19.1561 | 11.1466 | Last Calibration Date: | 2022-12-12
[7 empty] | Mass Flow Deviation [kg/hr] | -0.022 | -0.017685
[7 empty] | Mass Flow Deviation [%] | -0.11485 | -0.15866 | Total Result from all tests
[10 empty] | Average Mass Flow Deviation [%] | -0.13675
[7 empty] | 42FIT4000 - Totalizer [kg] | 3.1894 | 1.8704 | Average Totalizer Deviation [%] | -0.75727
[7 empty] | Ext. Flow - Totalizer [kg] | 3.2271 | 1.8769 | Total Deviation Meas/Actual [%] | -0.44701
[7 empty] | Totalizer Deviation [kg] | -0.0377 | -0.0065
[7 empty] | Totalizer Deviation [%] | -1.1682 | -0.34632 | FlowMeas / FlowActual [%] | 99.8632
[10 empty] | TotalizerMeas / TotalizerActual [%] | 99.2427
[7 empty] | 42FIT4000 - Temperature [℃] | 15.22 | 15.3 | Combined result of FlowMeas and TotalizerMeas [%] | 99.553
[7 empty] | Ext. Flow - Temperature [℃] | 16.32 | 16.36 | Total Deviation Ratio Meas/Actual | 0.99553
[7 empty] | Ext. Flow - Density [kg/m3] | 1164.6 | 1164.2
Accuracy test: | 2 | Note:
Date | 2024-02-27
Flowtransmitter | 42FIT4000
Chemical name | Scale inhibitor A
Last tested | 2023-03-13
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 35 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
1 | 12.4352 | 11.1231 | N/A |  |  |  | Setpoint Pump Stroke Length [%]
2 | 11.8543 | 11.1351 | N/A
3 | 12.3561 | 11.1564 | N/A | Zero calibrated 42FIT4000 |  |  | 42FIT4000 - Mass Flow [kg/hr]
4 | 12.1957 | 11.1153 | N/A |  |  |  | Ext. Flow - Mass Flow [kg/hr]
5 | 11.8525 | 11.1399 | N/A |  |  |  | Mass Flow Deviation [kg/hr]
6 | 12.3563 | 11.1274 | N/A |  |  |  | Mass Flow Deviation [%]
7 | 12.1654 | 11.1453 | N/A
8 | 11.9543 | 11.1642 | N/A |  |  |  | 42FIT4000 - Totalizer [kg]
9 | 12.1295 | 11.1346 | N/A |  |  |  | Ext. Flow - Totalizer [kg]
10 | 12.0564 | 11.1265 | N/A |  |  |  | Totalizer Deviation [kg]
Totalizer Deviation [%]
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1164 | 15 | 16.2 |  |  |  | 42FIT4000 - Temperature [℃]
2 | [6 empty] | Ext. Flow - Temperature [℃]
3 | 1164 | 15.1 | 16.1 |  |  |  | Ext. Flow - Density [kg/m3]
4
5 | 1165 | 15 | 16.1
6
7 | 1164 | 15.1 | 16.1
8
9 | 1165 | 15 | 16.2
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 12.1356 | 11.1368
Average Temperature [℃] | 15.04 | 16.14
Average Density [kg/m3] | N/A | 1164.4
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 2.041 | 1.874
Totalizer [L] | #DIV/0! | 1.6094
Results Flowglass
Volume delivered from Flowglass [L] | N/A
Results of adjustments
Accuracy test: | 3 | Note:
Date | 2024-02-27
Flowtransmitter | 42FIT4000
Chemical name | Scale inhibitor A
Last tested | 2023-03-13
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 50 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
0 | 19.1359 | 19.1534 | N/A | Zero calibrated |  |  | Setpoint Pump Stroke Length [%]
0.5 | 19.1375 | 19.1599 | N/A
1 | 19.1274 | 19.1518 | N/A |  |  |  | 42FIT4000 - Mass Flow [kg/hr]
1.5 | 19.1312 | 19.1606 | N/A | Damping for 42FIT: 0 secs --> 20 secs |  |  | Ext. Flow - Mass Flow [kg/hr]
2 | 19.1381 | 19.1527 | N/A | Filter Display tau: 0 --> 20 secs |  |  | Mass Flow Deviation [kg/hr]
2.5 | 19.1423 | 19.1563 | N/A | Filter Frequency tau: 0 --> 20 secs |  |  | Mass Flow Deviation [%]
3 | 19.135 | 19.1532 | N/A | Damping for Ext. Fit: 10 secs --> 20 secs
3.5 | 19.1412 | 19.1574 | N/A |  |  |  | 42FIT4000 - Totalizer [kg]
4 | 19.1245 | 19.1581 | N/A |  |  |  | Ext. Flow - Totalizer [kg]
4.5 | 19.1399 | 19.1557 | N/A |  |  |  | Totalizer Deviation [kg]
5 | 19.1241 | 19.1546 | N/A |  |  |  | Totalizer Deviation [%]
5.5 | 19.1403 | 19.1589 | N/A
6 | 19.1258 | 19.1592 | N/A |  |  |  | 42FIT4000 - Temperature [℃]
6.5 | 19.1374 | 19.1548 | N/A |  |  |  | Ext. Flow - Temperature [℃]
7 | 19.1265 | 19.1554 | N/A |  |  |  | Ext. Flow - Density [kg/m3]
7.5 | 19.1419 | 19.1551 | N/A
8 | 19.1367 | 19.1559 | N/A
8.5 | 19.1331 | 19.1544 | N/A
9 | 19.1298 | 19.1575 | N/A
9.5 | 19.1325 | 19.1562 | N/A
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1164 | 15.3 | 16.3
2
3 | 1165 | 15.3 | 16.3
4
5 | 1165 | 15.2 | 16.3
6
7 | 1164 | 15.1 | 16.3
8
9 | 1165 | 15.2 | 16.4
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 19.1341 | 19.1561
Average Temperature [℃] | 15.22 | 16.32
Average Density [kg/m3] | N/A | 1164.6
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 3.1894 | 3.2271
Totalizer [L] | 2.5951 | 2.771
Results Flowglass
Volume delivered from Flowglass [L] | N/A
Accuracy test: | 4 | Note:
Date | 2024-02-27
Flowtransmitter | 42FIT4000
Chemical name | Scale inhibitor A
Last tested | 2023-03-13
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 35 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
0 | 11.1368 | 11.1502 | N/A |  |  |  | Setpoint Pump Stroke Length [%]
0.5 | 11.1223 | 11.1426 | N/A
1 | 11.1204 | 11.1427 | N/A |  |  |  | 42FIT4000 - Mass Flow [kg/hr]
1.5 | 11.14 | 11.1418 | N/A |  |  |  | Ext. Flow - Mass Flow [kg/hr]
2 | 11.1317 | 11.1514 | N/A |  |  |  | Mass Flow Deviation [kg/hr]
2.5 | 11.1185 | 11.1486 | N/A |  |  |  | Mass Flow Deviation [%]
3 | 11.1269 | 11.1433 | N/A
3.5 | 11.1394 | 11.1446 | N/A |  |  |  | 42FIT4000 - Totalizer [kg]
4 | 11.1278 | 11.1497 | N/A |  |  |  | Ext. Flow - Totalizer [kg]
4.5 | 11.1331 | 11.1467 | N/A |  |  |  | Totalizer Deviation [kg]
5 | 11.1355 | 11.1442 | N/A |  |  |  | Totalizer Deviation [%]
5.5 | 11.1164 | 11.1461 | N/A
6 | 11.1303 | 11.1491 | N/A |  |  |  | 42FIT4000 - Temperature [℃]
6.5 | 11.1345 | 11.1443 | N/A |  |  |  | Ext. Flow - Temperature [℃]
7 | 11.1372 | 11.1519 | N/A |  |  |  | Ext. Flow - Density [kg/m3]
7.5 | 11.1238 | 11.1463 | N/A
8 | 11.1216 | 11.1494 | N/A
8.5 | 11.1241 | 11.1487 | N/A
9 | 11.1295 | 11.1455 | N/A
9.5 | 11.1289 | 11.1453 | N/A
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1164 | 15.3 | 16.3
2
3 | 1165 | 15.3 | 16.3
4
5 | 1164 | 15.4 | 16.4
6
7 | 1164 | 15.3 | 16.3
8
9 | 1164 | 15.2 | 16.5
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 11.1289 | 11.1466
Average Temperature [℃] | 15.3 | 16.36
Average Density [kg/m3] | N/A | 1164.2
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 1.8704 | 1.8769
Totalizer [L] | 1.5219 | 1.6122
Results Flowglass
Volume delivered from Flowglass [L] | N/A