## Deviation test 42FIT4018 (2)
Flowmeter | Tank ID | Chemical | Injectionpoint | Range 4 mA [kg/hr] | Range 20 mA [kg/hr] | Density SAS
42FT4018 | 42TB007 | Flocculant | 2. Trinn Separator Gjøa | 0 | 3 | 1.013
Accuracy test: | 1 | Note:
Date | 2024-02-26
Flowtransmitter | 42FIT4018
Chemical name | Flocculant
Last tested | 2019-03-31
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 20 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 20 |  | 5. Reset the totalizer before each test
BEFORE ADJUSTMENTS
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x] | Test [1] | Test [2] | Date of Test: | 2024-02-26
1 | 1.5657 | 1.7435 | 2400 |  |  |  | Setpoint Pump Stroke Length [%] | 20 | 70 | Flow Transmitter: | 42FIT4018
2 | 1.5592 | 1.7438 |  | The 20 mA range could be higher, the pump gives 7,6 kg/hr at 70% | [5 empty] | Flow Measurement Range: | 0 - 3,0 kg/hr
3 | 1.5338 | 1.7785 |  |  |  |  | 42FIT4018 - FlowMeas [kg/hr] | 1.5457 | 6.7163 | Last Calibration Date: | 2019-03-31
4 | 1.4025 | 1.7777 |  | Zero calibrated Ext. Flowmeter |  |  | Ext. Flow - FlowActual [kg/hr] | 1.7649 | 7.6133 | Coriolis Sensor Fabric New | 2016-04-04
5 | 1.6742 | 1.7799 |  |  |  |  | Mass Flow Deviation [kg/hr] | -0.21926 | -0.89705
6 | 1.536 | 1.7123 |  |  |  |  | Mass Flow Deviation [%] | -12.4232 | -11.7826 | Total Result from all tests
7 | 1.532 | 1.7781 | [7 empty] | Average Mass Flow Deviation [%] | -12.1029
8 | 1.5271 | 1.7733 |  |  |  |  | 42FIT4018 - TotalizerMeas [kg] | 0.2609 | 1.1833 | Average Totalizer Deviation [%] | -8.5918
9 | 1.4809 | 1.7772 |  |  |  |  | Ext. Flow - TotalizerActual [kg] | 0.2929 | 1.2623 | Total Deviation Meas/Actual [%] | -10.3474
10 | 1.6453 | 1.785 | 2685 |  |  |  | Totalizer Deviation [kg] | -0.032 | -0.079
[7 empty] | Totalizer Deviation [%] | -10.9252 | -6.2584 | Flow-glass / TotalizerActual Accuracy [%] | 99.9287
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1023 | 13 | 13.6 |  |  |  | Flow-glass Volume injected [L] | 0.285 | 1.24 | FlowMeas / FlowActual [%] | 87.8971
2 | [6 empty] | Flow-glass Mass injected [kg] | 0.29133 | 1.2673 | TotalizerMeas / TotalizerActual [%] | 91.4082
3 | 1022 | 13 | 13.6 |  |  |  | Flow-glass/TotalizerActual Deviation [%] | -0.53704 | 0.39452 | Combined result of FlowMeas and TotalizerMeas [%] | 89.6526
4 | [9 empty] | Total Deviation Ratio Meas/Actual | 0.89653
5 | 1022 | 13.1 | 13.6 |  |  |  | 42FIT4018 - Temperature [℃] | 13.06 | 13.72
6 | [6 empty] | Ext. Flow - Temperature [℃] | 13.6 | 13.66
7 | 1022 | 13.1 | 13.6 |  |  |  | Ext. Flow - Density [kg/m3] | 1022.2 | 1022
8
9 | 1022 | 13.1 | 13.6
10 | [6 empty] | Settings | Before | Calculated
[7 empty] | Flow Calibration Factor [kg/s2] | 236.3077 | 263.5814
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 1.5457 | 1.7649 | [5 empty] | Before | After
Average Temperature [℃] | 13.06 | 13.6 |  |  |  |  | Fine adjustments for FCF [kg/s2] | 263.5814 | 264.9
Average Density [kg/m3] | N/A | 1022.2
[7 empty] | Other Settings | Before | After
[7 empty] | Damping tau Analog Out [sec] | 0 | 10
Note: The totalizer is manually checked on both flowmeters at approximately minute 10. | [6 empty] | Damping filter for Local Display [sec] | 0 | 10
Results | 42FITXXXX | Extern flowmeter |  |  |  |  | Damping Samles [Samples] | 50 | 65
Totalizer [kg] | 0.2609 | 0.2929 |  |  |  |  | Filter Frequency tau [sec] | 0 | 10
Totalizer [L] | 0.25755 | 0.28654 |  |  |  |  | Density Measurement | On | Off
Results Flowglass
Volume delivered from Flowglass [L] | 0.285 | [5 empty] | AFTER ADJUSTMENTS:
[7 empty] | Average values for Deviation Test [x] | Test [3] | Test [4]
[7 empty] | Setpoint Pump Stroke Length [%] | 25 | 60 | Date of Test: | 2024-02-26
[10 empty] | Flow Transmitter: | 42FIT4018
[7 empty] | 42FIT4018 - Mass Flow [kg/hr] | 1.3152 | 6.1642 | Flow Measurement Range: | 0 - 3,0 kg/hr
[7 empty] | Ext. Flow - Mass Flow [kg/hr] | 1.3241 | 6.2146 | Last Calibration Date: | 2019-03-31
[7 empty] | Mass Flow Deviation [kg/hr] | -0.008895 | -0.05043
[7 empty] | Mass Flow Deviation [%] | -0.67178 | -0.81147 | Total Result from all tests
[10 empty] | Average Mass Flow Deviation [%] | -0.74163
[7 empty] | 42FIT4018 - Totalizer [kg] | 0.2134 | 1.0229 | Average Totalizer Deviation [%] | -1.2848
[7 empty] | Ext. Flow - Totalizer [kg] | 0.217 | 1.0323 | Total Deviation Meas/Actual [%] | -1.0132
[7 empty] | Totalizer Deviation [kg] | -0.0036 | -0.0094
[7 empty] | Totalizer Deviation [%] | -1.659 | -0.91059 | Flow-glass / TotalizerActual [%] | 99.4477
[7 empty] | Flow-glass Volume injected [L] | 0.21 | 1.01 | FlowMeas / FlowActual [%] | 99.2584
[7 empty] | Flow-glass Mass injected [kg] | 0.21462 | 1.0322 | TotalizerMeas / TotalizerActual [%] | 98.7152
[7 empty] | 42FIT4018 Flow-glass/Totalizer Deviation [%] | -1.0968 | -0.0077497 | Combined result of FlowMeas and TotalizerMeas [%] | 98.9868
[10 empty] | Total Deviation Ratio Meas/Actual | 0.98987
[7 empty] | 42FIT4018 - Temperature [℃] | 13 | 14.04
[7 empty] | Ext. Flow - Temperature [℃] | 14.28 | 14.1
[7 empty] | Ext. Flow - Density [kg/m3] | 1022 | 1022
Accuracy test: | 2 | Note:
Date | 2024-02-26
Flowtransmitter | 42FIT4018
Chemical name | Flocculant
Last tested
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 70 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 20 |  | 5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
1 | 6.8252 | 7.6042 | 1800 |  |  |  | Setpoint Pump Stroke Length [%]
2 | 6.7081 | 7.6211
3 | 6.7629 | 7.6316 |  | Zero Calibrated 42FIT4018 |  |  | 42FIT4018 - Mass Flow [kg/hr]
4 | 6.6409 | 7.613 |  |  |  |  | Ext. Flow - Mass Flow [kg/hr]
5 | 6.6708 | 7.6158 |  |  |  |  | Mass Flow Deviation [kg/hr]
6 | 6.7098 | 7.6054 |  |  |  |  | Mass Flow Deviation [%]
7 | 6.7246 | 7.5997
8 | 6.663 | 7.6097 |  |  |  |  | 42FIT4018 - Totalizer [kg]
9 | 6.7123 | 7.6017 |  |  |  |  | Ext. Flow - Totalizer [kg]
10 | 6.7452 | 7.6311 | 3040 |  |  |  | Totalizer Deviation [kg]
Totalizer Deviation [%]
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1022 | 13.8 | 13.6 |  |  |  | 42FIT4018 - Temperature [℃]
2 | [6 empty] | Ext. Flow - Temperature [℃]
3 | 1022 | 13.8 | 13.6 |  |  |  | Ext. Flow - Density [kg/m3]
4 | [6 empty] | Flow-glass Volume injected [L]
5 | 1022 | 13.8 | 13.7 |  |  |  | Flow-glass Mass injected [kg]
6
7 | 1022 | 13.6 | 13.7 |  |  |  | 42FIT4018 Flow-glass/Totalizer Deviation [%]
8
9 | 1022 | 13.6 | 13.7
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 6.7163 | 7.6133
Average Temperature [℃] | 13.72 | 13.66
Average Density [kg/m3] | N/A | 1022
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 1.1833 | 1.2623
Totalizer [L] | 1.1681 | 1.2351
Results Flowglass
Volume delivered from Flowglass [L] | 1.24
Results of adjustments
Accuracy test: | 3 | Note:
Date | 2024-02-27
Flowtransmitter | 42FIT4018
Chemical name | Flocculant
Last tested
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 25 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 15 |  | 5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
0 | 1.242 | 1.3331 | 1810 | Zero calibrated |  |  | Setpoint Pump Stroke Length [%]
0.5 | 1.2953 | 1.3254
1 | 1.1812 | 1.3251 |  |  |  |  | 42FIT4018 - Mass Flow [kg/hr]
1.5 | 1.2922 | 1.321 |  | Damping for 42FIT: 5 secs --> 20 secs |  |  | Ext. Flow - Mass Flow [kg/hr]
2 | 1.2258 | 1.3204 |  | Filter Display tau: 10 --> 20 secs |  |  | Mass Flow Deviation [kg/hr]
2.5 | 1.2292 | 1.3201 |  | Damping samples: 50 --> 80 samples |  |  | Mass Flow Deviation [%]
3 | 1.2499 | 1.319 |  | Filter Frequency tau: 10 --> 20 secs
3.5 | 1.3609 | 1.3182 |  |  |  |  | 42FIT4018 - Totalizer [kg]
4 | 1.3427 | 1.3251 |  |  |  |  | Ext. Flow - Totalizer [kg]
4.5 | 1.35 | 1.3253 |  | Damping for Ext. Fit: 10 secs --> 20 secs |  |  | Totalizer Deviation [kg]
5 | 1.321 | 1.3241 |  |  |  |  | Totalizer Deviation [%]
5.5 | 1.3108 | 1.3203
6 | 1.475 | 1.3224 |  |  |  |  | 42FIT4018 - Temperature [℃]
6.5 | 1.385 | 1.3245 |  |  |  |  | Ext. Flow - Temperature [℃]
7 | 1.422 | 1.3273 |  |  |  |  | Ext. Flow - Density [kg/m3]
7.5 | 1.375 | 1.3283 |  |  |  |  | Flow-glass Volume injected [L]
8 | 1.36 | 1.3253 |  |  |  |  | Flow-glass Mass injected [kg]
8.5 | 1.2612 | 1.325
9 | 1.2297 | 1.3252 |  |  |  |  | 42FIT4018 Flow-glass/Totalizer Deviation [%]
9.5 | 1.395 | 1.3267 | 2020
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1022 | 13 | 14.3
2
3 | 1022 | 13 | 14.3
4
5 | 1022 | 13 | 14.2
6
7 | 1022 | 13 | 14.3
8
9 | 1022 | 13 | 14.3
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 1.3152 | 1.3241
Average Temperature [℃] | 13 | 14.28
Average Density [kg/m3] | N/A | 1022
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 0.2134 | 0.217
Totalizer [L] | 0.21066 | 0.21233
Results Flowglass
Volume delivered from Flowglass [L] | 0.21
Accuracy test: | 4
Date | 2024-02-27
Flowtransmitter | 42FIT4018
Chemical name | Flocculant
Last tested
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 60 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 15 |  | 5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
0 | 6.1782 | 6.201 | 1600 |  |  |  | Setpoint Pump Stroke Length [%]
0.5 | 6.1571 | 6.2103
1 | 6.128 | 6.2065 |  |  |  |  | 42FIT4018 - Mass Flow [kg/hr]
1.5 | 6.0778 | 6.2072 |  |  |  |  | Ext. Flow - Mass Flow [kg/hr]
2 | 6.0818 | 6.2009 |  |  |  |  | Mass Flow Deviation [kg/hr]
2.5 | 6.1307 | 6.2059 |  |  |  |  | Mass Flow Deviation [%]
3 | 6.1896 | 6.2096
3.5 | 6.2119 | 6.2196 |  |  |  |  | 42FIT4018 - Totalizer [kg]
4 | 6.2516 | 6.2148 |  |  |  |  | Ext. Flow - Totalizer [kg]
4.5 | 6.2511 | 6.2162 |  |  |  |  | Totalizer Deviation [kg]
5 | 6.2419 | 6.211 |  |  |  |  | Totalizer Deviation [%]
5.5 | 6.1811 | 6.2204
6 | 6.1907 | 6.2284 |  |  |  |  | 42FIT4018 - Temperature [℃]
6.5 | 6.181 | 6.2127 |  |  |  |  | Ext. Flow - Temperature [℃]
7 | 6.161 | 6.2262 |  |  |  |  | Ext. Flow - Density [kg/m3]
7.5 | 6.1568 | 6.227 |  |  |  |  | Flow-glass Volume injected [L]
8 | 6.1405 | 6.2083 |  |  |  |  | Flow-glass Mass injected [kg]
8.5 | 6.0832 | 6.2252
9 | 6.1366 | 6.2278 |  |  |  |  | 42FIT4018 Flow-glass/Totalizer Deviation [%]
9.5 | 6.1532 | 6.2134 | 2610
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1022 | 14.1 | 14
2
3 | 1022 | 14.1 | 14.1
4
5 | 1022 | 14 | 14.2
6
7 | 1022 | 14 | 14.1
8
9 | 1022 | 14 | 14.1
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 6.1642 | 6.2146
Average Temperature [℃] | 14.04 | 14.1
Average Density [kg/m3] | N/A | 1022
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 1.0229 | 1.0323
Totalizer [L] | 1.0098 | 1.0101
Results Flowglass
Volume delivered from Flowglass [L] | 1.01