## Deviation test 42FIT4023
Flowmeter | Tank ID | Chemical | Injectionpoint | Range 4 mA [kg/t] | Range 20 mA [kg/t] | Density SAS
42FT4023 | 42TB015 | Corrosion inhibitor | Oil export pipeline | 0 | 16.1 | 1.028
Accuracy test: | 1 | Note:
Date | 2024-02-25
Flowtransmitter | 42FIT4023
Chemical name | Corrosion inhibitor
Last tested | 2021-03-19
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 54 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 20 |  | 5. Reset the totalizer before each test
BEFORE ADJUSTMENTS
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x] | Test [1] | Test [2] | Date of Test: | 2024-02-25
1 | 6.4308 | 6.9 | 1600 | Zero calibrated Ext. Flowmeter |  |  | Setpoint Pump Stroke Length [%] | 54 | 75 | Flow Transmitter: | 42FIT4023
2 | 6.47 | 6.8832 | [7 empty] | Flow Measurement Range: | 0 - 16,10 kg/hr
3 | 7.042 | 6.8945 |  |  |  |  | 42FIT4023 - FlowMeas [kg/hr] | 6.8005 | 10.0659 | Last Calibration Date: | 2021-03-19
4 | 7.3241 | 6.9038 |  |  |  |  | Ext. Flow - FlowActual [kg/hr] | 6.8799 | 10.2032 | Coriolis Sensor Fabric New | 2009-07-20
5 | 7.4038 | 6.8858 |  |  |  |  | Mass Flow Deviation [kg/hr] | -0.0794 | -0.13734
6 | 6.9162 | 6.8675 |  |  |  |  | Mass Flow Deviation [%] | -1.1541 | -1.346 | Total Result from all tests
7 | 6.7355 | 6.8658 | [7 empty] | Average Mass Flow Deviation [%] | -1.2501
8 | 6.2151 | 6.87 |  |  |  |  | 42FIT4023 - TotalizerMeas [kg] | 1.1815 | 1.7023 | Average Totalizer Deviation [%] | -0.03957
9 | 6.608 | 6.8656 |  |  |  |  | Ext. Flow - TotalizerActual [kg] | 1.1919 | 1.6889 | Total Deviation Meas/Actual [%] | -0.64482
10 | 6.8599 | 6.8632 | 2750 |  |  |  | Totalizer Deviation [kg] | -0.0104 | 0.0134
[7 empty] | Totalizer Deviation [%] | -0.87256 | 0.79342 | Flow-glass / TotalizerActual Accuracy [%] | 100.2475
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1039 | 14.2 | 14 |  |  |  | Flow-glass Volume injected [L] | 1.15 | N/A | FlowMeas / FlowActual [%] | 98.7499
2 | [6 empty] | Flow-glass Mass injected [kg] | 1.1948 | N/A | TotalizerMeas / TotalizerActual [%] | 99.9604
3 | 1039 | 14.3 | 14.1 |  |  |  | Flow-glass/TotalizerActual Deviation [%] | 0.2475 | N/A | Combined result of FlowMeas and TotalizerMeas [%] | 99.3552
4 | [9 empty] | Total Deviation Ratio Meas/Actual | 0.99355
5 | 1039 | 14.3 | 14.1 |  |  |  | 42FIT4023 - Temperature [℃] | 14.3 | 13.82
6 | [6 empty] | Ext. Flow - Temperature [℃] | 14.1 | 14.4
7 | 1039 | 14.3 | 14.1 |  |  |  | Ext. Flow - Density [kg/m3] | 1039 | 1039.4
8
9 | 1039 | 14.4 | 14.2
10 | [6 empty] | Settings | Before | Calculated
[7 empty] | Flow Calibration Factor [kg/s2] | 226.593 | 228.0636
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 6.8005 | 6.8799 | [5 empty] | Before | After
Average Temperature [℃] | 14.3 | 14.1 |  |  |  |  | Fine adjustments for FCF [kg/s2] | 228.0636 | 230.39
Average Density [kg/m3] | N/A | 1039
[7 empty] | Other Settings | Before | After
[7 empty] | Damping tau Analog Out [sec] | 0 | 10
Note: The totalizer is manually checked on both flowmeters at approximately minute 10. | [6 empty] | Damping filter for Local Display [sec] | 0 | 10
Results | 42FITXXXX | Extern flowmeter |  |  |  |  | Damping Samles [Samples] | 50 | 65
Totalizer [kg] | 1.1815 | 1.1919 |  |  |  |  | Filter Frequency tau [sec] | 0 | 10
Totalizer [L] | 1.1493 | 1.1472 |  |  |  |  | Density Measurement | On | Off
Results Flowglass
Volume delivered from Flowglass [L] | 1.15 | [5 empty] | AFTER ADJUSTMENTS:
[7 empty] | Average values for Deviation Test [x] | Test [3] | Test [4] | Date of Test: | 2024-02-25
[7 empty] | Setpoint Pump Stroke Length [%] | 80 | 54 | Flow Transmitter: | 42FIT4023
[10 empty] | Flow Measurement Range: | 0 - 16,10 kg/hr
[7 empty] | 42FIT4023 - Mass Flow [kg/hr] | 10.9559 | 6.8208 | Last Calibration Date: | 2021-03-19
[7 empty] | Ext. Flow - Mass Flow [kg/hr] | 10.9551 | 6.8233
[7 empty] | Mass Flow Deviation [kg/hr] | 0.00079 | -0.0025 | Total Result from all tests
[7 empty] | Mass Flow Deviation [%] | 0.0072113 | -0.036639 | Average Mass Flow Deviation [%] | -0.014714
[10 empty] | Average Totalizer Deviation [%] | -0.04801
[7 empty] | 42FIT4023 - Totalizer [kg] | 1.8241 | 1.1421 | Total Deviation Meas/Actual [%] | -0.031362
[7 empty] | Ext. Flow - Totalizer [kg] | 1.8233 | 1.1437
[7 empty] | Totalizer Deviation [kg] | 0.0008 | -0.0016 | FlowMeas / FlowActual [%] | 99.9853
[7 empty] | Totalizer Deviation [%] | 0.043876 | -0.1399 | TotalizerMeas / TotalizerActual [%] | 99.952
[10 empty] | Combined result of FlowMeas and TotalizerMeas [%] | 99.9686
[7 empty] | 42FIT4023 - Temperature [℃] | 13.92 | 13.76 | Total Deviation Ratio Meas/Actual | 0.99969
[7 empty] | Ext. Flow - Temperature [℃] | 14.5 | 14.46
[7 empty] | Ext. Flow - Density [kg/m3] | 1039.6 | 1039.8
Accuracy test: | 2 | Note:
Date | 2024-02-25
Flowtransmitter | 42FIT4023
Chemical name | Corrosion inhibitor
Last tested | 2021-03-19
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 75 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 20 |  | 5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
1 | 10.0432 | 10.154 | N/A |  |  |  | Setpoint Pump Stroke Length [%]
2 | 10.3252 | 10.164 | N/A | Zero calibrated 42FIT4023
3 | 10.3456 | 10.188 | N/A |  |  |  | 42FIT4023 - Mass Flow [kg/hr]
4 | 9.9865 | 10.176 | N/A |  |  |  | Ext. Flow - Mass Flow [kg/hr]
5 | 9.7532 | 10.214 | N/A |  |  |  | Mass Flow Deviation [kg/hr]
6 | 9.9854 | 10.235 | N/A |  |  |  | Mass Flow Deviation [%]
7 | 10.4523 | 10.227 | N/A
8 | 9.8547 | 10.224 | N/A |  |  |  | 42FIT4023 - Totalizer [kg]
9 | 9.8532 | 10.23 | N/A |  |  |  | Ext. Flow - Totalizer [kg]
10 | 10.0593 | 10.22 | N/A |  |  |  | Totalizer Deviation [kg]
Totalizer Deviation [%]
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1040 | 13.8 | 14.5 |  |  |  | 42FIT4023 - Temperature [℃]
2 | [6 empty] | Ext. Flow - Temperature [℃]
3 | 1040 | 13.8 | 14.5 |  |  |  | Ext. Flow - Density [kg/m3]
4
5 | 1039 | 13.9 | 14.3
6
7 | 1039 | 13.8 | 14.4
8
9 | 1039 | 13.8 | 14.3
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 10.0659 | 10.2032
Average Temperature [℃] | 13.82 | 14.4
Average Density [kg/m3] | N/A | 1039.4
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 1.7023 | 1.6889
Totalizer [L] | 1.6559 | 1.6249
Results Flowglass
Volume delivered from Flowglass [L] | N/A
Results of adjustments
Accuracy test: | 3 | Note:
Date | 2024-02-25
Flowtransmitter | 42FIT4023
Chemical name | Corrosion inhibitor
Last tested | 2021-03-19
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 80 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 20 |  | 5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
1 | 10.952 | 10.9543 | N/A |  |  |  | Setpoint Pump Stroke Length [%]
2 | 10.9599 | 10.9528 | N/A | Damping(Samples): 50 --> 65
3 | 10.9554 | 10.9498 | N/A | Filter Display: 0-->20-->10 sec |  |  | 42FIT4023 - Mass Flow [kg/hr]
4 | 10.9487 | 10.9602 | N/A | Frequency damping tau: 0-->20-->10 sec |  |  | Ext. Flow - Mass Flow [kg/hr]
5 | 10.9534 | 10.9541 | N/A | Analog output Damping tau: -->20-->10 sec |  |  | Mass Flow Deviation [kg/hr]
6 | 10.9612 | 10.954 | N/A |  |  |  | Mass Flow Deviation [%]
7 | 10.9453 | 10.9549 | N/A | K Factor: 226,593 -->230,39 kg/s2
8 | 10.9637 | 10.9599 | N/A |  |  |  | 42FIT4023 - Totalizer [kg]
9 | 10.9623 | 10.9498 | N/A |  |  |  | Ext. Flow - Totalizer [kg]
10 | 10.9568 | 10.961 | N/A |  |  |  | Totalizer Deviation [kg]
Totalizer Deviation [%]
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1040 | 13.8 | 14.6 |  |  |  | 42FIT4023 - Temperature [℃]
2 | [6 empty] | Ext. Flow - Temperature [℃]
3 | 1039 | 14 | 14.5 |  |  |  | Ext. Flow - Density [kg/m3]
4
5 | 1041 | 13.9 | 14.6
6
7 | 1039 | 13.8 | 14.4
8
9 | 1039 | 14.1 | 14.4
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 10.9559 | 10.9551
Average Temperature [℃] | 13.92 | 14.5
Average Density [kg/m3] | N/A | 1039.6
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 1.8241 | 1.8233
Totalizer [L] | 1.7744 | 1.7538
Results Flowglass
Volume delivered from Flowglass [L] | N/A
Accuracy test: | 4 | Note:
Date | 2024-02-25
Flowtransmitter | 42FIT4023
Chemical name | Corrosion inhibitor
Last tested | 2021-03-19
1. Firstly warm up the system and stabilize the system with the regulator in manual.
Key settings |  |  | 2. Start the flow comparrison and note every 1 minute the actual kg/hr flow from the Flow Meters.
Setpoint stroke length [%] | 54 |  | 3. Use the Flow Glass as tank if possible.
Regulator [Man/Auto] | Manual |  | 4. Use same filter settings for External and Internal flow meter.
Filter time locally for both [sec] | 20 |  | 5. Reset the totalizer before each test
Time [minute] | 42FITXXXX [kg/hr] | Extern flowmeter [kg/hr] | Flow glass [ml] | Notes [Faults found] |  |  | Average values for Deviation Test [x]
1 | 6.869 | 6.81 | N/A |  |  |  | Setpoint Pump Stroke Length [%]
2 | 6.816 | 6.843 | N/A
3 | 6.824 | 6.821 | N/A |  |  |  | 42FIT4023 - Mass Flow [kg/hr]
4 | 6.896 | 6.809 | N/A |  |  |  | Ext. Flow - Mass Flow [kg/hr]
5 | 6.725 | 6.785 | N/A |  |  |  | Mass Flow Deviation [kg/hr]
6 | 6.728 | 6.829 | N/A |  |  |  | Mass Flow Deviation [%]
7 | 6.715 | 6.788 | N/A
8 | 6.877 | 6.878 | N/A |  |  |  | 42FIT4023 - Totalizer [kg]
9 | 6.866 | 6.893 | N/A |  |  |  | Ext. Flow - Totalizer [kg]
10 | 6.892 | 6.777 | N/A |  |  |  | Totalizer Deviation [kg]
Totalizer Deviation [%]
Time [minute] | Density Extern flowmeter [kg/m3] | Temp 42FITXXXX [℃] | Temp Extern flowmeter [℃]
1 | 1041 | 13.8 | 14.7 |  |  |  | 42FIT4023 - Temperature [℃]
2 | [6 empty] | Ext. Flow - Temperature [℃]
3 | 1040 | 13.7 | 14.6 |  |  |  | Ext. Flow - Density [kg/m3]
4
5 | 1039 | 13.9 | 14.3
6
7 | 1040 | 13.6 | 14.4
8
9 | 1039 | 13.8 | 14.3
10
Results | 42FITXXXX | Extern flowmeter
Average Mass flow [kg/hr] | 6.8208 | 6.8233
Average Temperature [℃] | 13.76 | 14.46
Average Density [kg/m3] | N/A | 1039.8
Note: The totalizer is manually checked on both flowmeters at approximately minute 10.
Results | 42FITXXXX | Extern flowmeter
Totalizer [kg] | 1.1421 | 1.1437
Totalizer [L] | 1.111 | 1.0999
Results Flowglass
Volume delivered from Flowglass [L] | N/A